October 2009

MANAGER'S REPORT

The following is a brief summary of activities related to the Authority during the last month, including but not limited to, the following items:

Administrative Items

American Canyon Sanitary Landfill

Two of the off site methane monitoring probes have had continuous readings above the required limits.  The readings do not cause a major concern since methane cannot migrate through water which now surrounds the entire landfill.  It does however cause a regulatory violation and requires action.  Efforts to extract additional methane from the area have resulted in one well to now have continued readings below the action level but the other continued above action levels.   Additional actions were taken to extract methane directly from the problem probe.  Early results are the levels are now below the action levels.   The probe will continue to be monitored to see if methane levels rise.

Loop Trail and public access

City of American Canyon (CAC) consultants are preparing the necessary maps and agreements to execute a lot line adjustment to assure the trail and Authority facilities will be on the appropriate property or easement, as well as providing a public trail around the landfill.  The City is expected to take action on the proposed documents October 6, 2009.  A tentative the date of November 5, 2009 has been set for the Authority Board to consider the agreements.

Microturbine Project

Shaw Environmental is reviewing the configuration and equipment of the landfill skid. An onsite inspection by Shaw’s John Burns produced a few ideas that could solve the condensate problem.  He suggested a minor rerouting of the inlet gas line that would allow for more condensate drainage to the condensate sump before the gas gets to the compressor station.  He also believes that the existing condensate trap is too small and too close to such a high capacity compressor to be effective in removing condensate as demonstrated by the current problems.  He also believes that some of the pipe modifications that have been made to return condensate back into the gas inlet as opposed to the condensate sump are counter productive.  Adding a coalescing filter as suggested by SCS may not be a problem solver.  But sloping the inlet gas line downhill is a good SCS suggestion.  Shaw’s suggested modification to the gas line follows the same simple principle but more effectively placed.  He has the ops manual for the unit and will review it for other suggestions.  He will send the unit layout figures to their compressor skid specialists for their comments as well.  We hope to have their final comments by the end of the week.

P3 Renewable Energy

Board Member Luce will be touring the KDV facility in Tarragona, Spain at the end of October.

Solar Farm at ACSL

The Manager and Counsel facilitated a meeting with the Napa County Conservation, Development, and Planning Department to assist Green Tech Power Group, LLC in obtaining a Napa County Use Permit.  A project planner will be assigned to assist Green Tech Power in the processing of the permit.  Additionally our landfill consulting firm will be meeting with Green Tech Power to facilitate a design with minimal effects to the landfill environmental control systems and potential changes to the landfill’s post closure plan.

Capital Improvement Projects

- American Canyon Sanitary Landfill  Electrification

The electrical sub site walk is scheduled for the week of OCT 12th.

- Devlin Road Transfer Station Floor Resurfacing

The Authority’s five year plan is to replace the transfer station floor in Fiscal Year 2010-11.  Staff is monitoring the floor to ensure that wear does not cause damage beyond the current estimated cost in resurfacing.  Delta Pacific will be updating the last assessment of floor condition performed in 2007.