AMERICAN CANYON SANITARY Landfill AIR COMPLIANCE REPORT july 2005

Prepared for

Napa-Vallejo Waste Management Authority

1195 Third Street, Room 101

Napa, California 94559

August 12, 2005

Prepared by

EMCON/OWT, Inc.

4005 Port Chicago Highway

Concord, CA 94520

- Contents

1	introduction	1

1.1	Purpose	1

1.2	Record Keeping and Reporting	1

1.3	Report Preparation	1

2	routine operations & maintenance	2

2.1	Backup Flare Operations	2

2.1.1	Backup Flare Downtime	2

2.1.2	Collection System Downtime	2

2.1.3	    Backup Flare Maintenance	3

2.1.4	Landfill Gas Flow Rate	3

2.2	Wellfield Operations	3

2.2.1	Wellfield Deviations	3

2.2.2	Wellfield Maintenance	5

2.2.3	Leachate Treatment	5

2.3	Monthly Cover Integrity Inspection	6

2.4	Surface Emissions Monitoring	7

2.5	Component Leak Testing	7

3	additional MAINTENANCE AND EMERGENCy callouts	8

3.1	Additional Maintenance	8

3.1.1	Rapid Oxidation Monitoring	8

3.1.2	Shallow Soaker Well System	8

3.2	Emergency Callouts	9

4	COMPLIANCE 	10

4.1	Backup Flare Operations	10

4.2	Wellfield Operations	10

4.3	Monthly Cover Integrity Inspection	10

4.4	Surface Emissions Monitoring	10

4.5	Component Leak Testing	11

appendix A

A-2 Flare Temperature Deviation and Missing Data Log

APPENDIX B

A-2 Flare Downtime Log – SSMP

appendix C

GCCS Downtime Summary

APPENDIX D

GRS Engine Number 1 Downtime Log

APPENDIX E

GRS Engine Number 2 Downtime Log

APPENDIX F

A-2 Backup Flare Monthly Flow Rate Report

APPENDIX G

Annual Flare Heat Input Calculations

APPENDIX H

Monthly Wellfield Readings

APPENDIX I

Wellfield Deviations and 15-Day Remonitoring Readings

APPENDIX J

Well Disconnection Log – SSMP

APPENDIX K

Leachate Treatment Summary 2005

APPENDIX L

Cover Integrity Monitoring Log

APPENDIX M

CO Monitoring Data

APPENDIX N

120-Day Well Repair List

APPENDIX O

BAAQMD Correspondence

# 1	introduction

## 1.1	Purpose

The purpose of this monthly report is to document compliance with 40 Code of Federal Regulations (CFR) Part 60, Subpart Cc, Emission Guidelines (EG) for municipal solid waste landfills, and Bay Area Air Quality Management District (BAAQMD) Regulation 8 Rule 34 (8-34) requirements for operation and maintenance of the landfill gas collection and control system (GCCS) and the other compliance systems at the Napa-Vallejo Waste Management Authority’s (NVWMA’s) American Canyon Sanitary Landfill (ACSL).

The NVWMA operates ACSL as BAAQMD plant number 9183, and contracts with EMCON/OWT to operate the GCCS, including the flare, but not including the two Internal Combustion (IC) Engines.  Gas Recovery Systems, Inc. (GRS) owns and operates the IC Engines at the facility as BAAQMD plant number 11671 under a Gas Rights Agreement.

## 1.2	Record Keeping and Reporting

Records are maintained and available for inspection in accordance with BAAQMD Rule 8-34-501.12 and 40 CFR §60.758.  The primary location for the records storage will be in the Napa County Environmental Management Department located at 1195 Third Street, Room 101, Napa, California 94559.  The records will be maintained at this location for a period of five years.

## REPORT PREPARATION

This monthly report for the landfill and GCCS operations at the landfill has been prepared by EMCON/OWT, Inc, as authorized by NVWMA under the Operation and Maintenance contract between NVWMA and EMCON/OWT, Inc.  This monthly report was prepared based on EMCON/OWT’s review of information pertaining to the site operations.

# 2	routine operations & maintenance

In accordance with 40 CFR §60.757(f) and BAAQMD Regulation 8-34-411, an annual report is required to be submitted from applicable facilities containing performance and monitoring data for the operation of the GCCS.  This section pertains to the operations of the GCCS.

## 2.1	BACKUP FLARE OPERATIONS

This section contains information on the operation and maintenance of the flare (A-2).  General procedures at ACSL are for the landfill gas (LFG) to be abated by the GRS IC Engines.  If the engines shut down for any reason, then the flare is used to abate the LFG.

## 2.1.1	Backup Flare Downtime

During the month of July 2005, the A-2 flare operated a total of 83.7 hours out of 744 possible hours.  The A-2 flare is a back-up emission control device that primarily operates when one or more GRS IC Engines are not operating.  Pursuant to BAAQMD Regulation 8-34-501.2, the flare temperature was monitored and recorded.

The flare temperature deviation and missing data log is included in Appendix A.  As determined by a review of the paper chart recorder, there were no temperature deviations or periods of missing data during the month of July 2005.  See section 2.1.4 for a discussion of the landfill gas flow rate to the backup flare.

The Flare Downtime Log and the Startup, Shutdown, Malfunction (SSM) Forms, including dates, times, length of shut downs, and reasons for the shutdowns, are included in Appendix B of this report.

| ###### A-2 Flare |  |
| --- | --- |
| TOTAL RUNTIME (HOURS): | 83.7 |
| TOTAL DOWNTIME (HOURS): | 660.3 |
| RUNTIME PERCENTAGE: | 11.2% |

## Collection System Downtime

The landfill GCCS downtime is defined as any time that all three emission control devices are not operating.  There was no time during the month of July 2005 when at least one control device was not operating.

The calendar year total of GCCS downtime is 24.4 hours out of 240 hours allowable for the year pursuant to BAAQMD Regulation 8-34-113, Limited Exemption, Inspection and Maintenance.  The GCCS Downtime Summary for 2005 is included in Appendix C of this report.

In addition, the July 2005 GRS Engine Number 1 Downtime Log and the July 2005 GRS Engine Number 2 Downtime Log are included in Appendices D and Appendix E, respectively.

## 2.1.3	Backup Flare Maintenance

There were no additional A-2 backup flare maintenance activities to report during the month of July 2005.

## 2.1.4	Landfill Gas Flow Rate to Backup Flare

The monthly landfill gas flow rates and British thermal unit (Btu) calculations for the A-2 Backup Flare are included in Appendix F (8-34-501.5).  Annual backup flare heat input calculations are included in Appendix G.  The heat input to the backup flare did not exceed 576 million Btu per day, as required by Title V permit condition 12418 part 7, at any time during the month of July 2005.

Below are the total LFG volume, total methane (CH4) volume, and total heat input for the backup flare during July 2005:

| Source | Total Runtime (hours) | Total Downtime (hours) | CH4a (%) | Average Flow (scfm) | Total LFG Volume (scf) | Total CH4 Volume (scf) | Total Heat Input (MMBtu) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A-2 Flare | 83.7 | 660.3 | 52.6 | 531.2 | 2,666,921 | 1,402,800 | 1,421 |

a = percent methane as determined by most recent flare source test 52.6% on March 9, 2005

scfm = standard cubic feet per minute

scf = standard cubic feet

MMBtu = million British thermal units

## 2.2	WELLFIELD OPERATIONS

The wellfield was monitored July 13th and 14th, 2005.  The wellfield readings are located in Appendix H.

## 2.2.1	Wellfield Deviations

Pursuant to the BAAQMD Regulation 8-34-305 (Wellhead Requirements), each wellhead shall operate under a vacuum; wellhead temperature shall be less than 131 degrees F; and either the nitrogen concentration shall be less than 20 percent or the oxygen concentration shall be less than 5 percent.

There were eighteen well monitoring deviations during the month of July 2005.  Seven deviations were related to oxygen concentrations greater than 5 percent, ten deviations were for not operating under negative pressure, and one was for both oxygen concentrations greater than 5 percent and no negative pressure.  The Wellfield Deviation Log including the 15-day follow-up monitoring results is included in Appendix I.

Four of the eighteen wells were not in compliance during the 15-day remonitoring.  Two (GS-60 and GS-86) of the four wells were decommissioned on July 21, 2005 pursuant to Authority to Construct (ATC) Application No. 8677.  The initial July 2005 monitoring and remonitoring results are presented below for the four wells that deviated from the BAAQMD Regulation 8-34-305 (Wellhead Requirements) requirements:

| June Monitoring Date | Well ID # | Deviation | Comments | Remonitoring | Status | 120-Day List Repair Date |
| --- | --- | --- | --- | --- | --- | --- |
| 07/13/05 | L-33 | O2 = 19.6% | Well full of liquid/liquid to be pumped out | O2 = 19.1% on 07/20/05 | Non-Compliant; remains on the 120-day list | 08/11/05 |
| 07/14/05 | GS-60 | O2 = 7.6% | Air Leak Suspected | O2 = 5.9% on 07/20/05 | Decommissioned on 07/21/05 per ATC No. 8677 | N/A |
| 07/14/05 | GS-78 | O2 = 12.4% | Air leak suspected | O2 = 16.4% on 07/20/05 | Non-Compliant; remains on the 120-day list | 09/13/05 |
| 07/13/05 | GS-86 | O2 = 16.8% | Air leak suspected | O2 = 18.8% on 07/20/05 | Decommissioned on 07/21/05 per ATC No. 8677 | N/A |

O2 = oxygen

## 2.2.2	Wellfield Maintenance

The following wellfield maintenance activities were completed during the month of July 2005:

- July 13th and 14th, 2005 – EMCON/OWT conducted LFG well monitoring and minor maintenance and wellfield tuning;

- July 13th and 14th, 2005 – EMCON/OWT conducted the cap integrity inspection;

- July 20th, 2005 – EMCON/OWT conducted re-monitoring of the eighteen non-compliant LFG wells.

Permit Condition Number 12418 Part 4 requires that all of the wells be connected to and not isolated from the GCCS system unless one of the 8-34 exemptions applies. In addition, the BAAQMD provided a limited exemption from BAAQMD Regulation 8-34-117.5 that limits well disconnections to 24 consecutive hours or less in a May 21, 2004 letter to EMCON/OWT the NVWMA to disconnect wells for up to 5 days during final cap construction activities.  This limited exemption will expire on November 25, 2005.  BAAQMD Regulation 8-34-117.4 remains in effect - no more than 5 wells may be disconnected from the gas collection and control system at any one time.  All disconnections must be reported, even if the disconnections are for less than 24 hours.

A Well Disconnection Log based on the SSM is included in Appendix J.  No LFG wells were disconnected from the GCCS system during the month of July.  However, wells GS-60 and GS-86 were decommissioned on July 21, 2005 pursuant to ATC Application No. 8677.  The BAAQMD was notified of the decommissioning of wells GS-60 and GS-86 on July 21, 2005 via fax.  A copy of the submittal is included in Appendix O.

## 2.2.3	Leachate Treatment System

The leachate/condensate collection system is pumping from 13 leachate wells in the northern portion of the landfill (L-01, L-02, L-03, L-04, L-05, L-08, L-10, L-11, L-12, L-24, L-27, L-28 and L-32) and four condensate traps (CT-01, CT-02, CT-03 and CT-04).  The leachate/condensate summary tables are presented in Appendix K.

The remaining leachate pumps in the northern portion of the landfill are temporarily disconnected due to high chromium concentrations detected during leachate/condensate sampling, and are plumbed to the shallow soaker well system.  The leachate pumps in the cap construction area are temporarily disconnected due to cap construction activities. The leachate/condensate collection system will be shut down overnight and during weekends to prevent overfilling.

The leachate/condensate is collected in a tank farm near the GRS engine-house, and the leachate/condensate is hauled to the Vallejo Sanitation District (VSD) after sampling analytical approval.  EMCON/OWT samples the leachate/condensate, reviews the results, confirms compliance with VSD metal concentration limits, and informs Allied that VSD will accept the leachate/condensate.

Weekly records of leachate/condensate storage tanks throughput are determined by influent meter readings.  Monthly records of leachate pumped from each well are determined by wellhead counter readings.  The calendar year summary table presented below provides a comparison between the well counter readings and the leachate tank throughput readings.  The well counter readings are an estimate and do not represent the quantity of leachate removed from the site.

| Month | Monthly Leachate / Condensate Well Counter Readings (gallons) | Monthly Leachate / Condensate Storage Tank Throughput - (gallons) | Cumulative Leachate / Condensate Storage Tank Throughput (year to date gallons) | Monthly Leachate Shallow Soaker Well System Throughput (gallons) | Cumulative Leachate Shallow Soaker Well System Throughput (year to date gallons) |
| --- | --- | --- | --- | --- | --- |
| January 2005 | 86,098 | 81,794 | 81,794 | 0 | 0 |
| February 2005 | 64,645 | 102,566 | 184,360 | 198,360 | 198,360 |
| March 2005 | 142,677 | 141,394 | 325,744 | 131,632 | 329,992 |
| April 2005 | 55,771 | 147,350 | 473,094 | 206,541 | 563,533 |
| May 2005 | 104,698 | 94,843 | 567,947 | 217,021 | 780,554 |
| June 2005 | 129,321 | 73,403 | 641,340 | 248,475 | 1,029,029 |
| July 2005 | 43,481 | 65,210 | 706,650 | 117,104 | 1,146,133 |

The comparison of well counter totals and leachate/condensate storage tanks throughput totals provides a basis of confirmation for both sets of numbers.  EMCON/OWT conducts the well counter readings on or about the 20th of each month.  Allied records the leachate removed on or about the end of each month.  It is typical to have differences in the quantities measured because of differences in the times of measurement, and because of the assumption that each pump cycle produces 0.25 gallons.  The volume of discharge per pump cycle is variable, depending on the total dynamic head at each well, well efficiency, and air pressure.

## 2.3	MONTHLY COVER INTEGRITY INSPECTION

The landfill surface cover integrity was inspected on July 13th and 14th, 2005 pursuant to BAAQMD Regulation 8-34-510 (Cover Integrity Monitoring).  No problems were noted during the July 2005 monitoring event. The Cover Integrity Monitoring Log can be found in Appendix L.

## 2.4	SURFACE EMISSIONS MONITORING

Pursuant to BAAQMD Regulation 8-34-506 (Landfill Surface Monitoring), surface emissions monitoring (SEM) is to be completed at least once each quarter.  The 3rd quarter 2005 SEM event will be conducted during the month of August 2005.

## 2.5	COMPONENT Leak TESTING

Pursuant to BAAQMD Regulation 8-34-503 (Landfill Surface Monitoring), component leak testing is to be completed at least once each quarter.  The 3rd quarter 2005 component leak testing event will be conducted during the month of August 2005.

# 3	additional MAINTENANCE AND EMERGENCy callouts

The information included in this section describes additional non-routine maintenance that was performed during the month.  EMCON/OWT personnel completed the non-routine items listed here as part of our O&M contract.  This section also includes emergency callouts for the reporting month completed by EMCON/OWT personnel as part of our O&M contract.

## 3.1	ADDITIONAL MAINTENANCE

In addition to the routine compliance monitoring parameters, EMCON/OWT monitored LFG wells in the suspected rapid oxidation area for Carbon Monoxide (CO), temperature and vacuum, and installed and operated a shallow soaker well (SSW) system for leachate re-distribution.

## 3.1.1	Rapid Oxidation Monitoring

A rapid oxidation condition is suspected to have occurred in the area of the landfill around EW-13 and GS-85.  High CO concentrations could indicate rapid oxidation below the landfill cap.

EMCON/OWT monitored temperature and vacuum at the wells in the vicinity of EW-13 and GS-85 (including EW-13 and GS-85) on July 13th and 14th, 2005.  CO was monitored on July 25, 2005.  The vacuum has been reduced at each well in the vicinity as much as possible while maintaining negative pressure.  The CO Monitoring results can be found in Appendix M.

The temperature readings have been consistent at each well since monthly monitoring began April 22, 2004.  Monitoring indicates that a rapid oxidation condition may exist.  EMCON/OWT will continue to work with GRS to ensure that the LFG wells in the suspected rapid oxidation area are adjusted correctly.  If well readings show evidence of LFG over pull, then adjustments will be made.  LFG over pull can draw ambient air into the landfill and provide oxygen to fuel underground rapid oxidation conditions.

## 3.1.2	Shallow Soaker Well (SSW) System

The shallow soaker well (SSW) system is composed of three elements:

- Leachate extraction pumps (8) and re-distribution piping (from L-09, L-16, L-17, L-18, L-19, L-20, L-25 and L-26);

- The hydrosplitter; and

- Shallow “soaker” wells (15: SW-01, SW-02, SW-03, SW-04, SW-05, SW-06, SW-07, SW-08, SW-09, SW-10, SW-11, SW-12, SW-13, SW-14 and SW-15).

Continuous operation began February 7, 2005. The SSW system operated continuously between July 1, 2005 and July 31, 2005.

The SSW system total volume of liquid extracted between February 7, 2005 and July 14, 2005 is 1,146,133 gallons (according to leachate extraction pump counter readings and an estimated 0.25 gallons per count).  EMCON/OWT is monitoring water levels in the LFG wells surrounding the SSW system for signs of saturation; the water levels have not increased significantly since initial SSW system operation.

## 3.2	EMERGENCY CALLOUTS

There were no emergency callouts during the month of July 2005.

# 4	COMPLIANCE

This section contains detailed descriptions of the deviations as required from the site permits, BAAQMD Regulations including 8-34, NSPS/EG plans, and Title V requirements.

## 4.1	BACKUP FLARE OPERATIONS

There were no A-2 backup flare deviations during the month of July 2005.

## 4.2	WELLFIELD OPERATIONS

There were eighteen well monitoring deviations during the month of July 2005.  Seven deviations were related to oxygen concentrations greater than 5 percent, ten deviations were for not operating under negative pressure, and one was for both oxygen concentrations greater than 5 percent and no negative pressure.

Four of the eleven wells (L-33, GS-60, GS-78, and GS-86) were determined not to be in compliance during the 15-day remonitoring event.  Wells L-33 and GS-78 remain on the 120-Day repair list.  Wells GS-60 and GS-86 were decommissioned on July 21, 2005.  The 120-day correction and monitoring list is included in Appendix N.

## 4.3	MONTHLY COVER INTEGRITY INSPECTION

The landfill surface cover integrity inspection was conducted on July 13th and 14th, 2005 pursuant to BAAQMD Regulation 8-34-510 (Cover Integrity Monitoring).  No problems were noted during the July 2005 monitoring event.  The Cover Integrity Monitoring report can be found in Appendix L.

## 4.4	SURFACE EMISSIONS MONITORING

Pursuant to BAAQMD Regulation 8-34-506 (Landfill Surface Monitoring), surface emissions monitoring is to be completed at least once each quarter.  The 3rd quarter 2005 SEM event will be conducted during August 2005.

## 4.5	COMPONENT Leak TESTING

Pursuant to BAAQMD Regulation 8-34-503 (Landfill Surface Monitoring), component leak testing is to be completed at least once each quarter.  The 3rd quarter 2005 component leak testing event will be conducted during August 2005.

Appendix A

A-2 backup Flare tEMPERATURE Deviation and missing data lOG

APPENDIX B

A-2 BACKUP FLARE DOWNTIME LOG – SSMP

appendix C

GCCS DOWNTIME LOG

appendix D

GRs ENGINE #1 DOWNTIME LOG

appendix E

GRs ENGINE #2 DOWNTIME LOG

Appendix F

A-2 BACKUP FLARE Monthly FLOW RATE REPORT

appendix G

ANNUAL BACKUP FLARE Heat INPUT Calculations

APPENDIX H

MONTHLY WELLFIELD READINGS

appendix I

WELLFIELD DEVIATIONS AND 15-DAY REMONITORING READINGS

Appendix J

WELL Disconnection LOG – SSMP

APPENDIX K

LEACHATE TREATMENT SUMMARY 2004

APPENDIX L

COVER INTEGRITY MONITORING Log

APPENDIX M

co monitoring data

appendix n

120-day well repair list

appendix O

BAAQMD CORRESPONDENCE